## Read me
Model template
What this is |  | A starting point for your own model, with the same three parts as the example models: types, plant and bindings.
What is in it now |  | An invented wastewater example: a pumping station, a forcemain and part of a treatment plant. It matches examples/example-wastewater. Read it, then start your own in the blank copy (model-template-blank.xlsx).
Yellow cells |  | Yours to fill in. Most columns offer a drop-down list of the names already defined.
Grey cells |  | Formulas. Do not type in them. Each Check column shows "ok" or says what is wrong with that row.
Room |  | Each sheet checks rows 2 to 201. Start small: about ten assets is enough.
Topics |  | Built for you on the Bindings sheet, the same way as the example files: a measurement goes under the prefix below, then the asset's path and its short name; a state or alarm goes under the second prefix, then the top level, the asset and its short name. An asset can have a shorter name for topics. Nothing is typed twice.
Topic prefix for measurements | example/telemetry/wastewater | Change this to your own.
Topic prefix for states and alarms | example/events/wastewater | Change this to your own.
Which copy is the source |  | This spreadsheet is a starting point. Once the model is kept as files or in a tool, name that copy as the source and stop editing this one.
Never put in this file |  | Passwords, network addresses, real locations of critical equipment. If you fill in the Bindings sheet with real addresses, keep the file inside your organisation.
Left out to keep it small |  | Records such as procedures and drawings, quality limits, and derived values. The example files show how to add them later.
Everything here is invented |  | No name, tag, topic or value describes a real system.
Sheet | Rows filled | Rows with a problem
1 Types | 18 | 0
1 Measurement types | 12 | 0
1 Relationship types | 4 | 0
2 Assets | 20 | 0
2 Measurements | 17 | 0
2 Relationships | 13 | 0
3 Bindings | 17 | 0
All sheets | 101 | 0
Measurements not yet on the Bindings sheet | 0 | Not a problem during a first session. Fill these in afterwards.
What the checks catch |  | Names that do not match exactly (capitals count), duplicates, an asset with no parent that is not a site or network, a parent loop or more than five levels, a kind or measurement type that is not defined, a missing or wrong unit, and a topic used twice.
What they cannot catch |  | Whether a relationship is true, or whether a value is bound to the right address. Only people who know the plant can check that.

## 1 Types
Type | Is a kind of (extends) | What it means | Shared or local | Can sit at the top, with no parent | Standard followed, or to check first | Check (do not edit)
Location |  | A place: a site, a linear network, or a hydraulic region | Shared |  |  | ok
Function |  | A named slot in the site -> area -> equipment tree | Shared |  |  | ok
Asset |  | A physical thing with its own identity, installed at one Function | Shared |  |  | ok
Site | Location | ISA-95 site: a plant or a station | Shared | yes | ISA-95 equipment hierarchy | ok
Network | Location | A linear network (transmission mains) operated as one place | Shared | yes |  | ok
Area | Function | ISA-95 area: a process area of a site | Shared |  | ISA-95 equipment hierarchy | ok
Equipment | Function | A position in an area | Shared |  | ISA-95 equipment hierarchy (the levels below area) | ok
Reservoir | Equipment | A storage cell, clearwell or reservoir | Shared |  | Smart Data Models for water | ok
Pump | Equipment | A pump POSITION (duty role, run state, speed) | Shared |  | OPC 40223, OPC UA for Pumps and Vacuum Pumps | ok
Main | Equipment | A section of transmission main between two places | Shared |  | Smart Data Models for water | ok
Instrument | Asset | An online analyzer or transmitter | Shared |  | ISA-5.1, instrument symbols and identification | ok
WetWell | Reservoir | A chamber that collects sewage ahead of the pumps | Local |  |  | ok
Forcemain | Main | A pressurised sewer from a pumping station | Local |  |  | ok
Screen | Equipment | A screen that removes debris at the plant inlet | Local |  |  | ok
GritChamber | Equipment | A chamber where sand and grit settle out after screening | Local |  |  | ok
Blower | Equipment | A blower that supplies air to an aeration basin | Local |  |  | ok
AerationBasin | Equipment | A basin where air is added for biological treatment | Local |  |  | ok
Clarifier | Equipment | A tank where solids settle out | Local |  |  | ok

## 1 Measurement types
Measurement type | Kind | Unit (blank for a state or alarm) | What it means | Check (do not edit)
Pressure | Measurement | kPa | Water pressure | ok
Flow | Measurement | L/s | Volumetric flow rate | ok
Level | Measurement | m | Liquid level | ok
DissolvedOxygen | Measurement | mg/L | Dissolved oxygen | ok
DifferentialLevel | Measurement | m | Difference in level across a screen | ok
MotorCurrent | Measurement | A | Motor current | ok
PumpRunState | State or alarm |  | Pump run state | ok
PumpTripAlarm | State or alarm |  | Pump protection trip | ok
FailToStartAlarm | State or alarm |  | A machine was commanded to start and did not | ok
MainState | State or alarm |  | Operating state of a transmission main section | ok
HighLevelAlarm | State or alarm |  | Level above its alarm limit | ok
HighHighLevelAlarm | State or alarm |  | Level above its second, higher alarm limit | ok

## 1 Relationship types
Relationship | Its reverse | What it means | Check (do not edit)
Feeds | FedBy | The process stream (water or sewage) passes from one position to the next | ok
SuppliesAir | AirSuppliedBy | A compressor or blower supplies air to a vessel or basin | ok
Protects | ProtectedBy | A protective device guards a position (a surge vessel guards a main) | ok
Monitors | MonitoredBy | An instrument observes a position | ok

## 2 Assets
Asset ID | Display name | Type | Parent (blank only for a site or network) | Name in topics (optional; blank uses the ID) | Topic path (do not edit) | Check (do not edit) | Parent | Its parent | Next up | Next up | Too deep or a loop? | Top level
EXAMPLE_SPS | Example Sewage Pumping Station | Site |  |  | EXAMPLE_SPS | ok | [5 empty] | EXAMPLE_SPS
PUMPING | Wet well and pumps | Area | EXAMPLE_SPS |  | EXAMPLE_SPS/PUMPING | ok | EXAMPLE_SPS |  |  |  |  | EXAMPLE_SPS
WET_WELL | Wet well | WetWell | PUMPING |  | EXAMPLE_SPS/PUMPING/WET_WELL | ok | PUMPING | EXAMPLE_SPS |  |  |  | EXAMPLE_SPS
SP_01 | Sewage pump 1 | Pump | PUMPING |  | EXAMPLE_SPS/PUMPING/SP_01 | ok | PUMPING | EXAMPLE_SPS |  |  |  | EXAMPLE_SPS
SP_02 | Sewage pump 2 | Pump | PUMPING |  | EXAMPLE_SPS/PUMPING/SP_02 | ok | PUMPING | EXAMPLE_SPS |  |  |  | EXAMPLE_SPS
COLLECTION_A | Collection network A | Network |  | COLL_A | COLL_A | ok | [5 empty] | COLLECTION_A
FORCEMAINS_A | Forcemains | Area | COLLECTION_A |  | COLL_A/FORCEMAINS_A | ok | COLLECTION_A |  |  |  |  | COLLECTION_A
FORCEMAIN_A | Forcemain A (station to plant) | Forcemain | FORCEMAINS_A |  | COLL_A/FORCEMAINS_A/FORCEMAIN_A | ok | FORCEMAINS_A | COLLECTION_A |  |  |  | COLLECTION_A
EXAMPLE_WWTP | Example Wastewater Treatment Plant | Site |  |  | EXAMPLE_WWTP | ok | [5 empty] | EXAMPLE_WWTP
HEADWORKS | Headworks | Area | EXAMPLE_WWTP |  | EXAMPLE_WWTP/HEADWORKS | ok | EXAMPLE_WWTP |  |  |  |  | EXAMPLE_WWTP
PRIMARY | Primary treatment | Area | EXAMPLE_WWTP |  | EXAMPLE_WWTP/PRIMARY | ok | EXAMPLE_WWTP |  |  |  |  | EXAMPLE_WWTP
SECONDARY | Secondary treatment | Area | EXAMPLE_WWTP |  | EXAMPLE_WWTP/SECONDARY | ok | EXAMPLE_WWTP |  |  |  |  | EXAMPLE_WWTP
SCREEN_01 | Inlet screen 1 | Screen | HEADWORKS |  | EXAMPLE_WWTP/HEADWORKS/SCREEN_01 | ok | HEADWORKS | EXAMPLE_WWTP |  |  |  | EXAMPLE_WWTP
GRIT_01 | Grit chamber 1 | GritChamber | HEADWORKS |  | EXAMPLE_WWTP/HEADWORKS/GRIT_01 | ok | HEADWORKS | EXAMPLE_WWTP |  |  |  | EXAMPLE_WWTP
PRIMARY_01 | Primary settling tank 1 | Clarifier | PRIMARY |  | EXAMPLE_WWTP/PRIMARY/PRIMARY_01 | ok | PRIMARY | EXAMPLE_WWTP |  |  |  | EXAMPLE_WWTP
AERATION_01 | Aeration basin 1 | AerationBasin | SECONDARY |  | EXAMPLE_WWTP/SECONDARY/AERATION_01 | ok | SECONDARY | EXAMPLE_WWTP |  |  |  | EXAMPLE_WWTP
BLOWER_01 | Blower 1 | Blower | SECONDARY |  | EXAMPLE_WWTP/SECONDARY/BLOWER_01 | ok | SECONDARY | EXAMPLE_WWTP |  |  |  | EXAMPLE_WWTP
BLOWER_02 | Blower 2 | Blower | SECONDARY |  | EXAMPLE_WWTP/SECONDARY/BLOWER_02 | ok | SECONDARY | EXAMPLE_WWTP |  |  |  | EXAMPLE_WWTP
CLARIFIER_01 | Secondary clarifier 1 | Clarifier | SECONDARY |  | EXAMPLE_WWTP/SECONDARY/CLARIFIER_01 | ok | SECONDARY | EXAMPLE_WWTP |  |  |  | EXAMPLE_WWTP
AERATION_01_AIT | Aeration basin 1 oxygen probe | Instrument | AERATION_01 |  | EXAMPLE_WWTP/SECONDARY/AERATION_01/AERATION_01_AIT | ok | AERATION_01 | SECONDARY | EXAMPLE_WWTP |  |  | EXAMPLE_WWTP

## 2 Measurements
Measurement ID | Kind | Asset it belongs to | What it measures (from the Measurement types sheet) | Unit (blank for a state or alarm) | Short name (last part of the topic) | Display name | On the Bindings sheet? (do not edit) | Check (do not edit)
WET_WELL_LEVEL | Measurement | WET_WELL | Level | m | LEVEL | Wet well level | yes | ok
FORCEMAIN_A_PRESSURE | Measurement | FORCEMAIN_A | Pressure | kPa | PRESSURE | Forcemain A pressure | yes | ok
FORCEMAIN_A_FLOW | Measurement | FORCEMAIN_A | Flow | L/s | FLOW | Forcemain A flow | yes | ok
AERATION_01_DO | Measurement | AERATION_01 | DissolvedOxygen | mg/L | DO | Aeration basin 1 dissolved oxygen | yes | ok
SCREEN_01_DIFF_LEVEL | Measurement | SCREEN_01 | DifferentialLevel | m | DIFF_LEVEL | Inlet screen 1 differential level | yes | ok
SP_01_CURRENT | Measurement | SP_01 | MotorCurrent | A | CURRENT | Sewage pump 1 motor current | yes | ok
SP_02_CURRENT | Measurement | SP_02 | MotorCurrent | A | CURRENT | Sewage pump 2 motor current | yes | ok
WET_WELL_HIGH_LEVEL | State or alarm | WET_WELL | HighLevelAlarm |  | HighLevelAlarm | Wet well high-level alarm | yes | ok
WET_WELL_HIGH_HIGH_LEVEL | State or alarm | WET_WELL | HighHighLevelAlarm |  | HighHighLevelAlarm | Wet well high-high-level alarm | yes | ok
SP_01_RUN | State or alarm | SP_01 | PumpRunState |  | PumpRunState | Sewage pump 1 run state | yes | ok
SP_01_TRIP | State or alarm | SP_01 | PumpTripAlarm |  | PumpTripAlarm | Sewage pump 1 trip alarm | yes | ok
SP_02_RUN | State or alarm | SP_02 | PumpRunState |  | PumpRunState | Sewage pump 2 run state | yes | ok
SP_02_TRIP | State or alarm | SP_02 | PumpTripAlarm |  | PumpTripAlarm | Sewage pump 2 trip alarm | yes | ok
SP_01_FAIL_TO_START | State or alarm | SP_01 | FailToStartAlarm |  | FailToStartAlarm | Sewage pump 1 fail-to-start alarm | yes | ok
SP_02_FAIL_TO_START | State or alarm | SP_02 | FailToStartAlarm |  | FailToStartAlarm | Sewage pump 2 fail-to-start alarm | yes | ok
FORCEMAIN_A_STATE | State or alarm | FORCEMAIN_A | MainState |  | MainState | Forcemain A state | yes | ok
BLOWER_01_FAIL_TO_START | State or alarm | BLOWER_01 | FailToStartAlarm |  | FailToStartAlarm | Blower 1 fail-to-start alarm | yes | ok

## 2 Relationships
From (asset ID) | Relationship | To (asset ID) | Check (do not edit)
WET_WELL | Feeds | SP_01 | ok
WET_WELL | Feeds | SP_02 | ok
SP_01 | Feeds | FORCEMAIN_A | ok
SP_02 | Feeds | FORCEMAIN_A | ok
FORCEMAIN_A | Feeds | SCREEN_01 | ok
SCREEN_01 | Feeds | GRIT_01 | ok
GRIT_01 | Feeds | PRIMARY_01 | ok
PRIMARY_01 | Feeds | AERATION_01 | ok
AERATION_01 | Feeds | CLARIFIER_01 | ok
BLOWER_01 | SuppliesAir | AERATION_01 | ok
BLOWER_02 | SuppliesAir | AERATION_01 | ok
SCREEN_01 | Protects | GRIT_01 | ok
AERATION_01_AIT | Monitors | AERATION_01 | ok

## 3 Bindings
Measurement ID | Address at the source | Historian tag | Topic (built for you; do not edit) | Check (do not edit)
WET_WELL_LEVEL | ExampleSps.WetWell.Level | EXAMPLE_SPS.WET_WELL.LEVEL | example/telemetry/wastewater/EXAMPLE_SPS/PUMPING/WET_WELL/LEVEL | ok
FORCEMAIN_A_PRESSURE | CollA.ForcemainA.Pressure | COLL_A.FORCEMAIN_A.PRESSURE | example/telemetry/wastewater/COLL_A/FORCEMAINS_A/FORCEMAIN_A/PRESSURE | ok
FORCEMAIN_A_FLOW | CollA.ForcemainA.Flow | COLL_A.FORCEMAIN_A.FLOW | example/telemetry/wastewater/COLL_A/FORCEMAINS_A/FORCEMAIN_A/FLOW | ok
AERATION_01_DO | ExampleWwtp.Aeration01.Do | EXAMPLE_WWTP.AERATION_01.DO | example/telemetry/wastewater/EXAMPLE_WWTP/SECONDARY/AERATION_01/DO | ok
SCREEN_01_DIFF_LEVEL | ExampleWwtp.Screen01.DiffLevel | EXAMPLE_WWTP.SCREEN_01.DIFF_LEVEL | example/telemetry/wastewater/EXAMPLE_WWTP/HEADWORKS/SCREEN_01/DIFF_LEVEL | ok
SP_01_CURRENT | ExampleSps.Sp01.Current | EXAMPLE_SPS.SP_01.CURRENT | example/telemetry/wastewater/EXAMPLE_SPS/PUMPING/SP_01/CURRENT | ok
SP_02_CURRENT | ExampleSps.Sp02.Current | EXAMPLE_SPS.SP_02.CURRENT | example/telemetry/wastewater/EXAMPLE_SPS/PUMPING/SP_02/CURRENT | ok
WET_WELL_HIGH_LEVEL | ExampleSps.WetWell.HighLevelAlarm | EXAMPLE_SPS.WET_WELL.HIGH_LEVEL_ALARM | example/events/wastewater/EXAMPLE_SPS/WET_WELL/HighLevelAlarm | ok
WET_WELL_HIGH_HIGH_LEVEL | ExampleSps.WetWell.HighHighLevelAlarm | EXAMPLE_SPS.WET_WELL.HIGH_HIGH_LEVEL_ALARM | example/events/wastewater/EXAMPLE_SPS/WET_WELL/HighHighLevelAlarm | ok
SP_01_RUN | ExampleSps.Sp01.PumpRunState | EXAMPLE_SPS.SP_01.PUMP_RUN_STATE | example/events/wastewater/EXAMPLE_SPS/SP_01/PumpRunState | ok
SP_01_TRIP | ExampleSps.Sp01.PumpTripAlarm | EXAMPLE_SPS.SP_01.PUMP_TRIP_ALARM | example/events/wastewater/EXAMPLE_SPS/SP_01/PumpTripAlarm | ok
SP_02_RUN | ExampleSps.Sp02.PumpRunState | EXAMPLE_SPS.SP_02.PUMP_RUN_STATE | example/events/wastewater/EXAMPLE_SPS/SP_02/PumpRunState | ok
SP_02_TRIP | ExampleSps.Sp02.PumpTripAlarm | EXAMPLE_SPS.SP_02.PUMP_TRIP_ALARM | example/events/wastewater/EXAMPLE_SPS/SP_02/PumpTripAlarm | ok
SP_01_FAIL_TO_START | ExampleSps.Sp01.FailToStartAlarm | EXAMPLE_SPS.SP_01.FAIL_TO_START_ALARM | example/events/wastewater/EXAMPLE_SPS/SP_01/FailToStartAlarm | ok
SP_02_FAIL_TO_START | ExampleSps.Sp02.FailToStartAlarm | EXAMPLE_SPS.SP_02.FAIL_TO_START_ALARM | example/events/wastewater/EXAMPLE_SPS/SP_02/FailToStartAlarm | ok
FORCEMAIN_A_STATE | CollA.ForcemainA.MainState | COLL_A.FORCEMAIN_A.MAIN_STATE | example/events/wastewater/COLL_A/FORCEMAIN_A/MainState | ok
BLOWER_01_FAIL_TO_START | ExampleWwtp.Blower01.FailToStartAlarm | EXAMPLE_WWTP.BLOWER_01.FAIL_TO_START_ALARM | example/events/wastewater/EXAMPLE_WWTP/BLOWER_01/FailToStartAlarm | ok